## 2024-FULL
Dry Core Transformer Losses Proposed for 2024
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.2109 | 0.1192 |  | 6.0882
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.1588 | 10.8331 | 11.9919 | 0.97834 | 12.9702
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.545 | 14.4442 | 15.9892 | 1.3045 | 17.2936
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.9699 | 18.1712 | 20.1411 | 1.6632 | 21.8042
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.6265 | 25.0453 | 27.6719 | 2.2176 | 29.8895
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.1672 | 29.1203 | 32.2875 | 2.6741 | 34.9617
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.5512 | 32.5773 | 36.1285 | 2.9983 | 39.1267 |  | 2024 Proposed Rates
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.1908 | 38.3219 | 42.5127 | 3.5383 | 46.051 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.2144 | 47.5234 | 52.7378 | 4.4025 | 57.1403 | GS 50 to 1,499 kW | 0.02033 | 4.2259 | 2.4718 | 6.4215
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.3325 | 48.6137 | 53.9462 | 4.5023 | 58.4485 | GS 1,500 to 4,999 kW | 0.02173 | 4.3877 | 2.6418 | 5.9586
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.579 | 50.8734 | 56.4524 | 4.7103 | 61.1627 | Large Use | 0.02447 | 4.8641 | 2.9749 | 5.8845
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 5.9953 | 54.673 | 60.6683 | 5.0619 | 65.7302
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.4117 | 58.4725 | 64.8843 | 5.4134 | 70.2977
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 7.9567 | 72.9167 | 80.8734 | 6.7179 | 87.5913 | Tier 1 | 0.103 | November 1, 2023 Rate
500 KVA 1PH 1.2KV BIL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 KVA 1PH 1.2KV BIL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | Tier 2 | 0.125 | November 1, 2023 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.60334 | 5.8807 | 6.484 | 0.5094 | 6.9934
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.92702 | 8.9116 | 9.8386 | 0.78268 | 10.6213 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.854 | 17.8232 | 19.6773 | 1.5654 | 21.2426 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.3175 | 21.6662 | 23.9838 | 1.9567 | 25.9404 | RRRP | 0.0007
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.09 | 28.8883 | 31.9783 | 2.6089 | 34.5873
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.5578 | 43.1005 | 47.6583 | 3.8482 | 51.5065
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.5234 | 50.9025 | 56.4259 | 4.6634 | 61.0893
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 5.9834 | 55.5195 | 61.5029 | 5.0518 | 66.5547
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.4485 | 60.2005 | 66.649 | 5.4445 | 72.0935
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 6.9139 | 64.8827 | 71.7967 | 5.8375 | 77.6341
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.3817 | 79.0949 | 87.4767 | 7.0767 | 94.5534
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.0312 | 143.8562 | 157.8874 | 11.8466 | 169.734
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 15.9143 | 165.4433 | 181.3576 | 13.4365 | 194.7942
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 20.8583 | 209.7036 | 230.5619 | 17.6107 | 248.1726
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 23.4077 | 236.9682 | 260.3759 | 19.7632 | 280.1391
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 31.2874 | 314.5554 | 345.8428 | 26.4161 | 372.2589
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 37.3132 | 376.7706 | 414.0838 | 31.5037 | 445.5875
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 44.8068 | 453.198 | 498.0048 | 37.8306 | 535.8354
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 52.8412 | 536.1516 | 588.9928 | 44.614 | 633.6068
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 64.8928 | 660.582 | 725.4748 | 54.7892 | 780.2641
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 74.5496 | 763.1142 | 837.6639 | 62.9426 | 900.6064
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains May 1, 2022 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2022
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2024 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2024
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2023-0032
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.2109 | 0.1192 |  | 6.0882
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.1588 | 10.8331 | 11.9919 | 0.97834 | 12.9702
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.545 | 14.4442 | 15.9892 | 1.3045 | 17.2936
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.9699 | 18.1712 | 20.1411 | 1.6632 | 21.8042
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.6265 | 25.0453 | 27.6719 | 2.2176 | 29.8895
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.1672 | 29.1203 | 32.2875 | 2.6741 | 34.9617
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.5512 | 32.5773 | 36.1285 | 2.9983 | 39.1267
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.1908 | 38.3219 | 42.5127 | 3.5383 | 46.051
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.2144 | 47.5234 | 52.7378 | 4.4025 | 57.1403
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.3325 | 48.6137 | 53.9462 | 4.5023 | 58.4485
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.579 | 50.8734 | 56.4524 | 4.7103 | 61.1627
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 5.9953 | 54.673 | 60.6683 | 5.0619 | 65.7302
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.4117 | 58.4725 | 64.8843 | 5.4134 | 70.2977
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 7.9567 | 72.9167 | 80.8734 | 6.7179 | 87.5913
500 KVA 1PH 1.2KV BIL | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 KVA 1PH 1.2KV BIL | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.60334 | 5.8807 | 6.484 | 0.5094 | 6.9934
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.92702 | 8.9116 | 9.8386 | 0.78268 | 10.6213
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.854 | 17.8232 | 19.6773 | 1.5654 | 21.2426
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.3175 | 21.6662 | 23.9838 | 1.9567 | 25.9404
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.09 | 28.8883 | 31.9783 | 2.6089 | 34.5873
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.5578 | 43.1005 | 47.6583 | 3.8482 | 51.5065
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.5234 | 50.9025 | 56.4259 | 4.6634 | 61.0893
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 5.9834 | 55.5195 | 61.5029 | 5.0518 | 66.5547
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.4485 | 60.2005 | 66.649 | 5.4445 | 72.0935
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 6.9139 | 64.8827 | 71.7967 | 5.8375 | 77.6341
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.3817 | 79.0949 | 87.4767 | 7.0767 | 94.5534
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.0312 | 143.8562 | 157.8874 | 11.8466 | 169.734
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 15.9143 | 165.4433 | 181.3576 | 13.4365 | 194.7942
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 20.8583 | 209.7036 | 230.5619 | 17.6107 | 248.1726
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 23.4077 | 236.9682 | 260.3759 | 19.7632 | 280.1391
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 31.2874 | 314.5554 | 345.8428 | 26.4161 | 372.2589
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 37.3132 | 376.7706 | 414.0838 | 31.5037 | 445.5875
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 44.8068 | 453.198 | 498.0048 | 37.8306 | 535.8354
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 52.8412 | 536.1516 | 588.9928 | 44.614 | 633.6068
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 64.8928 | 660.582 | 725.4748 | 54.7892 | 780.2641
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 74.5496 | 763.1142 | 837.6639 | 62.9426 | 900.6064
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard